ORCP-WR-WM-21-13

Date Received: 10 December 2021

REQUEST FOR MARKET RULES AND MANUALS AMENDMENTS

Proposals made only under this prescribed form shall be accepted and considered as submitted.

This request for amendments are be submitted to:

Rules Change Committee

Attention: WESM Governance Committee Secretariat

Philippine Electricity Market Corporation

18/F Robinsons Equitable Tower

ADB Avenue, Ortigas Center

Pasig City, 1605 Philippines

Email addresses: rcc@wesm.ph / mag_rrd@wesm.ph

Contact No: (+632) 8631-8734

- Proponent’s Information

| Name | Reynaldo B. Abadilla |
| --- | --- |
| Designation | OIC-Head, System Operations |
| Company | National Grid Corporation of the Philippines |
| Company Address | Quezon Avenue cor. BIR Road, Diliman, Quezon City, |
|  | Philippines |
| Telephone No. | 02 8863 7191 |
| Fax. No. |  |
| Email Address | rbabadilla@ngcp.ph |

- Amendment Information

Proposed Amendments to the (please tick the box):. WESM Rules Retail Rules. Market Manual:; System Security and Reliability Guidelines Issue 1.0 Dispatch Protocol Issue 16.0. Topic:; Enhancements in view of the Implementation of Reserve Market. Proposed Classification of Amendments (please tick the box): General Minor Urgent If Urgent, reason for urgency: _____________________________________________________________.

- SUMMARY OF THE PROPOSED RULES CHANGE

The proposed amendments to the WESM Rules and Manuals on Dispatch Protocol and System Security and Reliability Guidelines, aim to update and enhance the guidelines in view of various policy and regulatory issuances and the eventual implementation of the Reserve Market.

- BACKGROUND

The DOE issued DC2021-03-0009 which provided the framework for the implementation of the Reserve Market and provided further policies supplementing the policy on Ancillary Service (AS) utilization promulgated through DC2019-12-0018. The salient features of DC2021-03-009 are as follows:

- Guiding Principles

- Scope and Application

- Reserve Market Design

- Reserve Categories and Required Levels for the Initial implementation of the Reserve Market

- Reserve Market Participation Requirements

- Third-Party AS Capability Testing Entities

- Pricing and Cost Recovery

- Settlement

- Responsibilities of the System Operator, Market Operator, Governance Arm, and Ancillary Service Providers

- Regulatory Support

In compliance to DC2021-03-0009, the WESM Rules and Manuals are to be amended to incorporate the policies provided. The NGCP provided its comments and recommendations to an earlier proposal submitted by IEMOP. As identified and raised by the Rules Change Committee to the NGCP, the WESM Manual on System Security and Reliability Guidelines needs to be amended also to preserve system security and reliability in view of the implementation of the Reserve Market.

- THE PROPOSED RULES CHANGE

The main focus of the proposal is to enhance the guidelines and harmonize the provisions to the issued policies and regulatory issuances.

| No. | Proposed Change | WESM Manual |
| --- | --- | --- |
| 1 | Harmonization with the use of the Old Ancillary Service Categories per DC2021-03-0009 | System Security and Reliability Guidelines WESM Rules |
| 2 | Harmonization with the definitions and provisions of the Philippine Grid Code 2016 Edition | System Security and Reliability Guidelines WESM Rules Dispatch Protocol |
| 3 | Minor clerical and formatting changes | System Security and Reliability Guidelines |

- BACKGROUND AND DESCRIPTION OF THE PROPONENT

The proponent is the National Grid Corporation of the Philippines as the System Operator.

- CONCLUSIONS AND RECOMMENDATIONS

The amendments to the WESM Rules and Manual on System Security and Reliability Standards and Dispatch Protocol, aim to update and enhance the guidelines, consistent with the various policies and regulatory issuances to preserve system security and reliability in view of the implementation of the Reserve Market.

It is recommended that the proposed changes to be adopted.

- REFERENCES

- WESM Manual on System Security and Reliability Guidelines Issue 1.0

- WESM Rules

- WESM Manual on Dispatch Protocol Issue 16.0

- Philippine Grid Code 2016 Edition

- Proposed Amendments

- WESM Manual on System Security and Reliability Guidelines Issue 1.0

| Title | Clause | Provision | Proposed Amendment | Rationale | Comments | Proposed Wording based on Comments | Proponent’s Response | RCC Agreement |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Definition of Terms | Section2 | Automatic Generation Control (AGC). The regulation of the power output of generating units within a prescribed area in response to a change in system frequency, tie-line loading, or the relation of these to each other, so as to maintain the system frequency or the established interchange with other areas within the predetermined limits or both. | Propose to revise as follows: “Automatic Generation Control (AGC). It is an equipment that automatically adjusts the generation to maintain its generation dispatch, interchange schedule plus its share of frequency regulation. AGC is a combination of secondary control for a control area /control block and real-time operation of the generation dispatch function (based on generation scheduling). secondary control is operated by the System Operator while generation scheduling is operated by the respective generation companies. The regulation of the power output of generating units within a prescribed area in response to a change in system frequency, tie-line loading, or the relation of these to each other, so as to maintain the system frequency or the established interchange with other areas within the predetermined limits or both.” | For consistency with the definition in the PGC 2016 Edition. |  |  |  |  |
|  |  | Automatic Load Dropping (ALD). The process of automatically and deliberately removing pre-selected loads from a power system in response to an abnormal condition in order to maintain the integrity of the system. | Propose to revise as: “Automatic Load Dropping (ALD). The process of automatically and deliberately removing pre-selected loads from a power system in response to an abnormal condition in order to maintain the integrity of the system. It can be classified as: Under-Frequency Load Shedding (UFLS); and Under-Voltage Load Shedding (UVLS).” | For consistency with the definition on PGC2016 and Dispatch Protocol Issue 16.0. |  |  |  |  |
|  |  | Backup Reserve (also called cold standby reserve). Refers to a generating unit that has fast start capability and can synchronize with the grid to provide its declared capacity for a minimum period of eight (8) hours. | Propose to delete. | This reserve classification is no longer used in PGC 2016 edition. |  |  |  |  |
|  |  | Contingency. The unexpected failure or outage of a system component, such as a generator, transmission line, power transformer, bus, circuit breaker, or other electrical element. A contingency may also include multiple components, which are related by situations leading to simultaneous component outages. | Propose to revise as follows: “Contingency. The outage of a single component of the grid that cannot be predicted in advance but which excludes scheduled maintenance. The unexpected failure or outage of a system component, such as a generator, transmission line, power transformer, bus, circuit breaker, or other electrical element. A contingency may also include multiple components, which are related by situations leading to simultaneous component outages.” | For consistency with the definition in the PGC 2016. |  |  |  |  |
|  |  | Contingency Reserve. The generating capacity that is intended to take care of the loss of the largest synchronized generating unit or the power import from a single grid interconnection, whichever is larger. Contingency reserve includes spinning reserve and backup reserve. | Propose to revise as: “Contingency Reserve. The synchronized generating capacity from qualified generating units and qualified interruptible loads allocated to cover that is intended to take care of the loss or failure of the largest synchronized a generating unit or a transmission element or the power import from a circuit interconnection the power import from a single grid interconnection, whichever is larger. Contingency reserve includes spinning reserve and backup reserve.” | For consistency with the definition of Contingency Reserve based on DOE DC2021-03-0009. |  |  |  |  |
|  |  | NEW | Propose to add: “Critical Loading. This refers to the condition where the loading of transmission lines or substation equipment is between 90 percent and 100 percent of the continuous rating.” | For consistency with PGC2016 and in reference to the usage in Section 5.2 (d). |  |  |  |  |
|  |  | NEW | Propose to add: “Demand Control. The reduction in demand for the control of the frequency, when the grid is in an emergency state. This includes automatic load dropping, manual load dropping, demand reduction upon instruction by the System Operator and voluntary demand managament.” | For consistency with PGC2016 and in reference to the usage in Section 5. |  |  |  |  |
|  |  | NEW | Propose to add: “Dispatchable Reserve. Generating capacity that are readily available for dispatch in order to replenish the Contingency Reserves whenever a generating unit trips or a loss of a single transmission interconnection occurs.” | For consistency with DC2021-03-009 and in reference to the usage in Section 5. |  |  |  |  |
|  |  | NEW | Propose to add: “Imminent Overloading. The condition when the loading of transmission lines or substation Equipment is above 100 percent up to 110 percent of the continuous rating.” | For consistency with PGC2016 and in reference to the usage in Section 5.2 (d). |  |  |  |  |
|  |  | Island Grid. A portion of a power system or several power systems that is electrically separated from the interconnection due to the disconnection of transmission system elements. | Propose to revise: “Island Grid. A generating plant portion of a power system or a group of generating plants and its associated load, which is isolated from the rest of the grid but is capable of generating and maintaining a stable supply of electricity to customers within an isolated area several power systems that is electrically separated from the interconnection due to the disconnection of transmission system elements. | For consistency with PGC2016 and in reference to its usage in Section 5.11. |  |  |  |  |
|  |  | NEW | Propose to add: “Islanding Operation. The isolated operation of certain portions of the grid as a result of forced outages or contingency action by the System Operator.” | For consistency with PGC2016 and in reference to its usage in Sections 5.9 and 5.11. |  |  |  |  |
|  |  | Load Following and Frequency Regulating (LFFR) Reserve. The amount of generating capacity that provides for following the moment-to-moment variations in demand or supply in a power system and for maintaining acceptable system frequency. | Propose to revise as: Load Following and Frequency Regulating (LFFR) Reserve. The amount of generating capacity that provides for following the moment-to-moment variations in demand or supply in a power system and for maintaining acceptable system frequency. These are readily available and dispatchable generating capacity that is allocated exclusively to correct deviations from the acceptable nominal frequency caused by unpredicted variations in demand or generation output. | For consistency with the Regulating Reserve definition of the DOE DC2021-03-0009. |  |  |  |  |
|  |  | Manual Load Dropping (MLD). The process of manually and deliberately removing preselected loads from a power system in response to an abnormal condition in order to maintain the integrity of the system. | Propose to revise as: “Manual Load Dropping (MLD). The process of manually and deliberately removing preselected loads from a power system in response to an abnormal condition in order to maintain the integrity of the power system. | For consistency with PGC 2016 definition. |  |  |  |  |
|  |  | Multiple Outage Contingency. An event caused by the failure of two (2) or more components of the grid including generating units, transmission lines, and transformers. | Propose to revise as follows: Multiple Outage Contingency. An event caused by the failure of two (2) or more components of the grid including generating units, transmission lines, and transformers. | For consistency with the definition in PGC 2016. |  |  |  |  |
|  |  | Operating Margin. The margin of generation over the total demand plus losses that is necessary for ensuring power quality and the security of the grid. Operating margin is the sum of the load following and frequency regulating reserve and the contingency reserve. | Propose to revise as follows: “Operating Margin. The margin of generation over the total demand plus losses that is necessary for ensuring power quality and the security of the grid. Operating margin is the sum of the load following and frequency regulating reserve,and the contingency reserveThe available generating capacity in excess of the sum of the system demand plus losses within a specified period of time..” | For consistency with the definition of operating margin in PGC 2016. |  |  |  |  |
|  |  | NEW | Propose to add: “Net Operating Margin The available generating capacity in excess of the sum of the system demand plus losses and regulating reserve within a specified period of time.” | Introduced in reference to its use in Section 5.2 (a). |  |  |  |  |
|  |  | Security. The ability of the electric system to withstand sudden disturbances such as electric short circuits or unanticipated loss of system elements. | Proposed to revise as follows: “Security. The continuous operation of a power system in the normal state, ensuring safe and adequate supply of power to end-users, even when some parts or components of the system are on outageThe ability of the electric system to withstand sudden disturbances such as electric short circuits or unanticipated loss of system elements.” | For consistency with the definition used in PGC 2016 Edition. |  |  |  |  |
|  |  | Single Outage (N-1) Contingency. An event caused by the failure of one component of the grid including a generating unit, transmission line, or transformer. | Propose to revise as: “Single Outage (N-1) Contingency (N-1). An event caused by the failure outage of one component of the grid including: a generating unit, transmission line, or transformer.” (a) Loss of a single-circuit transmission line, except those radial circuits which connect Loads using a single line or cable; (b) Loss of one circuit of a double-circuit transmission line including the point-to-point connection of a Generating Plant to the Grid; (c) Loss of submarine cable; (d) Loss of a single Transformer, except those which connect Loads using a single radial Transformer; (e) Loss of a Generating Unit; and (f) Loss of compensating devices, i.e., Capacitor/Reactor/SVC | For consistency with the definition and Section 6.2.1.1 of the PGC 2016. |  |  |  |  |
|  |  | Spinning Reserve (also called hot standby reserve). The component of contingency reserve which is synchronized to the grid and ready to take on load. | Propose to delete. | This reserve type is no longer used in PGC 2016 edition. |  |  |  |  |
|  |  | System Integrity Protection Scheme (SIPS). A protection system that is designed to detect abnormal or predetermined system conditions, and take automatic corrective actions. | Revise as follows: “System Integrity Protection Scheme (SIPS). A protection system that is designed to detect abnormal or predetermined system conditions, and take automatic corrective actions other than and/or in addition to the isolation of faulted components in order to preserve the integrity of the power system or strategic portions thereof.” | For consistency with the definition under the PGC 2016. |  |  |  |  |
|  |  | Voltage Control. The control of transmission voltages through adjustments in generator reactive output and transformer taps and by switching capacitor and reactors on the transmission and distribution systems. | Propose to revise as: “Voltage Control. The control of transmission voltages through adjustments in generator reactive output and transformer taps and by switching capacitor and reactors on the transmission and distribution systems. Any actions undertaken by the System Operator or user to maintain the voltage of the Grid within the limits prescribed by the Philippine Grid Code such as, but not limited to, adjustment of generator reactive output, adjustment in transformer taps or switching of capacitors or reactors.” | For consistency with the definition on the PGC2016. |  |  |  |  |
| OBJECTIVE | Section 3 | Preservation of system reliability and security is the primary objective of these guidelines and is the responsibility of the System Operator. This mandate is clearly vested under Clause 3.8.2.1 (b) of the WESM Rules which stipulates that, during each trading interval, the System Operator shall use its reasonable endeavors to maintain system security consistent with the requirements of the Grid Code. Minimization of customer service interruptions and quick restoration of the power system to the normal state are secondary objectives of these guidelines. This document prescribes general guidelines that must be followed by all WESM Participants to maintain the security and reliability of the Luzon, Visayas and Mindanao power systems. These guidelines are based on existing practices and the Grid Code and Distribution Code requirements and developed in accordance with Clause 6.6.1.1 of the WESM Rules which states that the System Operator, in consultation with WESM Participants and the Market Operator, shall develop and periodically update system security and reliability guidelines, subject to approval of the PEM Board. These guidelines provide supplementary provisions for the improvement of WESM operations in ensuring the security and reliability of the grid. However, in case of conflict in the achievement of the objectives of the Grid Code, the provisions of the Grid Code shall prevail. | Propose to revise as: “Preservation of system reliability and security is the primary objective of these guidelines and is the responsibility of the System Operator. This mandate is clearly vested under Clause 3.8.2.1 (bc) of the WESM Rules which stipulates that, during each trading dispatch interval, the System Operator shall use its reasonable endeavors to maintain system security consistent with the requirements of the Grid Code. Minimization of customer service interruptions and quick restoration of the power system to the normal state are secondary objectives of these guidelines. xxx” | For consistency with the provisions of the WESM Rules. |  |  |  |  |
| Normal State Operation | 5.1 | The grid shall be operated so that it remains in the normal state, i.e.: - The operating margin is sufficient. - The grid frequency is within the limits as set forth in the Grid Code. - Voltages at all connection points are within the limits of 0.95 and 1.05 of the nominal value. - The loading levels of all transmission lines and transformers are below the limit as set forth in the Grid Code. - The grid configuration is such that any potential fault current can be interrupted and the faulted equipment can be isolated from the grid. - The static and dynamic stability of the power system is maintained. - The single outage contingency (N-1) criterion is met. | Propose to revise as follows: “5.1 Normal State Operation The Grid shall be considered to be in the Normal State when operated so that it remains in the normal state, i.e.: (a) The operating margin is sufficient. The Single Outage Contingency (N-1) Criterion is met; (b) The grid frequency is within the limits as set forth in the Grid Code. The Regulating, Contingency and Dispatchable Reserves are in accordance with the values established in the Ancillary Service Procurement Plan for these types of Reserves; (c) Voltages at all connection points are within the limits of 0.95 and 1.05 of the nominal value. The Grid Frequency is within the +/- 0.3 Hz limits. (d) The loading levels of all transmission lines and transformers are below the limit as set forth in the Grid Code. The voltages at all transmission substations are within 95% to 105% of the nominal voltage limits. (e) The grid configuration is such that any potential fault current can be interrupted and the faulted equipment can be isolated from the grid. The loading levels of all transmission lines and substation equipment are below 90% of the operational thermal limit capacity of phase conductors and transformers as certified and submitted by the Transmission Network Provider; and (f) The static and dynamic stability of the power system is maintained. The grid configuration is such that any potential fault current can be interrupted and the faulted equipment can be isolated from the grid. (g) The single outage contingency (N-1) criterion is met.” | For consistency with PGC2016 provisions regarding normal state on GO 6.2.2.1. For consistency with PGC 2016 6.2.21 (b). Revised PR and SR to RR CR, and included DR, for consistency with DC2021-03-009. For consistency with PGC2016 PST 3.2.2 and GCR 6.2.2.1(c). For consistency with PGC2016 PST 3.2.2 and GCR 6.2.2.1(d). In reference to PGC2016, GO 6.2.2.1 (e), originally 100% loading level, per PGC 2016. Proposed to be lowered to 90% to address conflicting interpretations in Alert State (Critical Loading = 90% to 100% loading). For consistency with PGC2016, GO 6.2.2.1 (f). |  |  |  |  |
| Alert State | 5.2 | The Grid shall be considered to be in the alert state when any one of the following conditions exists: (a) The voltages at the connection points are outside the limits of -5% and +5% but within the limits of -10% and +10% of the nominal value; (b) There is critical loading or imminent overloading of transmission lines or substation equipment; (c) A weather disturbance has entered the Philippine area of responsibility, which may affect grid operations; (d) Peace and order problems exist, which may pose a threat to grid operations; (e) The operating margin is not sufficient to replenish the sudden loss of the largest generating unit capacity synchronized to the grid; and (f) The grid frequency is beyond the limits of 59.7 Hz and 60.3 Hz but within the thresholds of 59.4 Hz and 60.6 Hz. | Propose to revise as follows: “5.2 Alert State The Grid shall be considered to be in the alert state when any one of the following conditions exists: (a) The voltages at the connection points are outside the limits of -5% and +5% but within the limits of -10% and +10% of the nominal value; The Single Outage Contingency (N-1) Criterion is not met; (b) There is critical loading or imminent overloading of transmission lines or substation equipment; The Regulating and Contingency Reserves are less than the values required to stabilize Frequency within the limits of 59.4 Hz and 60.6 Hz; (c) A weather disturbance has entered the Philippine area of responsibility, which may affect grid operations; The voltages at the Connection Points are outside the limits of 0.95 pu and 1.05 pu of the nominal value during N-0 conditions but within the limits of 0.90 pu and 1.10 pu of the nominal value; (d) Peace and order problems exist, which may pose a threat to grid operations; There is Critical Loading or Imminent Overloading of transmission lines or substation Equipment; (e) The operating margin is not sufficient to replenish the sudden loss of the largest generating unit capacity synchronized to the grid; and A weather disturbance has entered the Philippine area of responsibility, which may affect grid operations; or (f) The grid frequency is beyond the limits of 59.7 Hz and 60.3 Hz but within the thresholds of 59.4 Hz and 60.6 Hz. Peace and order problems exist, which may pose a threat to Grid operations.” | For consistency with PGC2016 GO 6.2.2.2. For consistency with PGC2016 GO 6.2.2.2 (a). For consistency with 6.2.2.2 (b). Revised Secondary and Primary Reserves to Regulating and Contingency Reserves , for consistency with DC2021-03-0009. For consistency with PGC2016 GO 6.2.2.2 (c). For consistency with PGC2016 GO 6.2.2.2 (d). For consistency with PGC2016 GO 6.2.2.2 (e). For consistency with PGC2016 GO 6.2.2.2 (f). |  |  |  |  |
| Emergency State | 5.3 | The grid shall be considered in the emergency state when: (a) Single outage contingency (N-1) criterion is not met. Imminent threat in system security would exist should a credible n-1 contingency occur that would result in the cascading outages of lines and equipment if not corrected immediately; (b) There is generation deficiency or operating margin is zero; (c) Grid transmission voltage is outside the limits of -10% or +10% of the nominal value; (d) The loading levels of all transmission lines and substation equipment are beyond the threshold as set by the Grid Code; and (e) The grid frequency is beyond the limits of 59.4 Hz and 60.6 Hz. | Propose to revise as follows: “5.3 Emergency State The grid shall be considered in the emergency state when either a Single Outage Contingency or a Multiple Outage Contingency has occurred without resulting in Total System Blackout, but any one of the following conditions exists: (a) Single outage contingency (N-1) criterion is not met. Imminent threat in system security would exist should a credible n-1 contingency occur that would result in the cascading outages of lines and equipment if not corrected immediately; There is generation deficiency or Operating Margin is zero; (b) There is generation deficiency or operating margin is zero; The grid transmission voltage is outside the limits of 0.90 or 1.10 pu of the nominal value; or (c) Grid transmission voltage is outside the limits of -10% or +10% of the nominal value; The loading level of any transmission line or substation Equipment is above 115% of its Operational Thermal Limit Capacity. (d) The loading levels of all transmission lines and substation equipment are beyond the threshold as set by the Grid Code; and (e) The grid frequency is beyond the limits of 59.4 Hz and 60.6 Hz.” | For consistency with PGC2016 GO 6.2.2.3 For consistency with PGC2016 GO 6.2.2.3 (a). For consistency with PGC2016 GO 6.2.2.3 (b). For consistency with PGC2016 GO 6.2.2.3 (c). |  |  |  |  |
| Single Outage (N-1) Contingency Criterion | 5.4 | Single Outage (N-1) Contingency Criterion (a) The security and reliability of the grid shall be based on the single outage contingency (N-1) criterion. This criterion specifies that the grid shall continue to operate in the normal state following the loss of one generating unit, transmission line, or transformer. (b) Credible single outage contingency (N-1) contingencies The N-1 Criterion is related to one of the following contingencies: (i) Loss of a single-circuit transmission line, except those radial circuits which connect loads using a single line or cable; (ii) Loss of one circuit of a double-circuit transmission line; (iii) Loss of submarine cable; (iv) Loss of a single transformer, except those which connect loads using a single radial transformer; (v) Loss of a generating unit, whether grid-connected or embedded; and (vi) Loss of compensating devices, i.e., capacitor / reactor / SVC (c) In the event of a credible N-1 contingency, the system or any part thereof shall be operated up to its operational thermal limit capacity, beyond which the System Operator shall intercept to restore system stability. For the avoidance of doubt, manual corrective interventions shall not be imposed to delimit the power transfer capabilities of equipment/transmission lines in anticipation of a secondary outage (N-1-1). However, if a significant threat to system security exists following the occurrence of a credible N-1 contingency the System Operator may intervene and shall make the necessary manual corrective actions as required, to protect the integrity of the grid. (d) The power system shall be operated at all times in such a manner that system instability, islanding, cascading outages, or voltage collapse will not occur as a result of the most severe single contingency. A single contingency may generally be assumed to mean the loss of a single system element; however, the outage of multiple system elements should be treated as a single contingency if caused by a single event of sufficiently high likelihood. (e) Multiple contingency outages of a credible nature shall be examined, and the system shall be operated to protect against system instability, islanding or cascading outages for these contingencies. (f) A planned activity notice or request for shutdown shall be issued by a grid user to the System Operator for any planned activity such as a planned shutdown or scheduled maintenance of its equipment at least seven (7) days prior to the actual shutdown or maintenance. This is to allow the System Operator sufficient time to evaluate if the planned outage can be accommodated by the power system and to coordinate the outage with other affected grid users. The System Operator shall notify the user of its approval or disapproval of the user’s request at least five (5) days before the actual work commences. | Propose to revise as: “5.4 Single Outage (N-1) Contingency (N-1) Criterion” xxx (b) Credible single outage contingency (N-1) contingencies The N-1 Criterion is related to one of the following contingencies: (i) Loss of a single-circuit transmission line, except those radial circuits which connect loads using a single line or cable; (ii) Loss of one circuit of a double-circuit transmission line;, including point-to-point connection of a generating plant to the grid; (iii) Loss of submarine cable; (iv) Loss of a single transformer, except those which connect loads using a single radial transformer; (v) Loss of a generating unit, whether grid-connected or embedded; and (vi) Loss of compensating devices, i.e., capacitor / reactor / SVC xxx (d) The power system shall be operated at all times in such a manner that system instability, islanding operation, cascading outages, or voltage collapse will not occur as a result of the most severe single contingency. A single contingency may generally be assumed to mean the loss of a single system element; however, the outage of multiple system elements should be treated as a single contingency if caused by a single event of sufficiently high likelihood. (e) Multiple contingency outages of a credible nature shall be examined, and the system shall be operated to protect against system instability, islanding operation or cascading outages for these contingencies. (f) A planned activity notice or request for shutdown shall be issued by a grid user to the System Operator and Market Operator for any planned activity such as a planned shutdown or scheduled maintenance of its equipment at least seven (7) days prior to the actual shutdown or maintenance. This is to allow the System Operator sufficient time to evaluate if the planned outage can be accommodated by the power system and to coordinate the outage with other affected grid users. The System Operator shall notify the user and the Market Operator of its approval or disapproval of the user’s request at least five (5) days before the actual work commences.” | For consistency with PGC2016 provisions. For consistency with PGC2016 GO 6.2.1 For consistency with the use of “islanding operations” in PGC 2016. For consistency with the use of “islanding operations” in PGC 2016. For consistency with PGC2016 GO 6.4.1.3. |  |  |  |  |
| Grid Operation Notices | 5.5 | The following notices shall be issued, without delay, by the System Operator to notify all grid users of an existing alert state: (a) Yellow alert when the contingency reserve is less than the capacity of the largest synchronized generating unit or power import from a single interconnection, whichever is higher; (b) Red alert when the contingency reserve is zero or generation deficiency exists or if there is critical loading or imminent overloading of transmission lines or equipment; For clarity, when the operating margin net of the regulating reserve capacity is less than the capacity of the largest synchronized generating unit or power import from a single interconnection, whichever is higher, the System Operator shall issue yellow alert notice. Likewise, if the operating margin less the regulating reserve capacity becomes zero, the System Operator shall issue red alert notice. (c) Weather disturbance alert when a weather disturbance has entered the Philippine area of responsibility; (d) Blue alert when a tropical disturbance is expected to make a landfall within twenty-four (24) hours; and (e) Security red alert when peace and order problem exist, which may affect the grid operations. | Propose to revise as: “5.5 xxx (a) Yellow alert when the contingency reserve is less than the capacity of the largest synchronized generating unit or power import from a single interconnection, whichever is higher; For clarity, when the net operating margin is less than the capacity of the largest synchronized generating unit or power import from a single interconnection, whichever is higher, the System Operator shall issue yellow alert notice. (b) Red alert when the contingency reserve is zero or generation deficiency exists or if there is critical loading or imminent overloading of transmission lines or equipment; For clarity, when the operating margin net of the regulating reserve capacity is less than the capacity of the largest synchronized generating unit or power import from a single interconnection, whichever is higher, the System Operator shall issue yellow alert notice. LikewiseFurther, if the operating margin less the regulating reserve capacity becomes zero, the System Operator shall issue red alert notice. (c)xxx (d)xxx (e)xxx” | Propose to revise wording for consistency and clarity with the description of Yellow and Red Alert states. |  |  |  |  |
| Voltage and Reactive Power Control | 5.6 | (a) The grid voltages shall be operated at safe levels to reduce the vulnerability of the grid to transient instability, dynamic instability, and voltage instability problems. Reactive reserve margins shall be adequate to maintain minimum acceptable voltage limits under facility outage conditions. (b) The control of voltage shall be achieved by managing the reactive power supply in the grid. These include the operation of the following equipment: (i) Synchronous generating units; (ii) Synchronous condensers; (iii) Shunt capacitors; (iv) Shunt reactors; (v) Static var compensators (SVCs); and (vi) On-load tap-changing transformers (c) Operation of static and dynamic reactive devices shall be coordinated such that static devices are switched in or out of service so that the maximum reactive reserves are maintained on generators, synchronous condensers and other dynamic reactive devices. (d) Reactive resources shall be dispersed and located electrically so that they can be applied effectively and quickly when contingencies occur. Sufficient reactive resources that are available and operable shall be ensured by the System Operator through its own facilities and by the procurement of reactive power support services. (e) As a last resort, especially during light load conditions, some transmission lines may be switched off to reduce the charging MVars (capacitive reactive power) in the system and to keep the voltages within allowable limits. Transmission lines may be removed from service only after studies indicate that system reliability will not be degraded below acceptable levels. (f) Necessary corrective actions, including load reduction, shall be taken to prevent voltage collapse when reactive resources are insufficient. (g) All generating units with automatic voltage control equipment shall normally be operated in voltage control mode. When a generator’s voltage regulator is out of service, field excitation shall be maintained at a level sufficient to maintain generator stability. | Propose to revise as follows: “xxx (b) In normal state, tThe control of voltage shall be achieved by managing the reactive power supply in the grid. These include the operation of the following equipment: (i) Synchronous generating units; (ii) Synchronous condensers; (iii) Shunt capacitors; (iv) Shunt reactors; (v) Static var compensators (SVCs); and (vi) On-load tap-changing transformers xxx” | For consistency with PGC2016 GO 6.7.1.1 |  |  |  |  |
| Frequency Control | 5.7 | (a) The grid frequency shall be controlled by the timely use of frequency regulating reserve, contingency reserve, and demand control such as automatic load dropping (ALD) and/or manual load dropping (MLD) during emergency conditions. (b) A generating unit providing regulating and/or contingency reserves may be operated either in an automatic frequency-sensitive mode (also known as free governor mode) with primary response or in an automatic generation control (AGC) mode with secondary response. (c) A generating unit providing primary response for frequency regulation as an ancillary service shall operate in an automatic frequency-sensitive mode (also known as free-governor mode) for automatic response of the unit’s power output to changes in frequency. The speed-governing system of the generating unit shall have a maximum response time of five (5) seconds. (d) Secondary response shall be required from selected generating units providing ancillary services for frequency regulation. Frequency control using the secondary response of the generating units shall be accomplished through automatic generation control (AGC) or manual adjustment of generation with specific dispatch instructions from the System Operator. The maximum response time for the change in the unit’s power output shall be twenty-five (25) seconds and which shall be sustainable for at least thirty (30) minutes. (e) The generation company or power plant shall not override the free-governor mode or automatic generation control (AGC) mode of a generating unit which is providing primary or secondary response. (f) Governors shall not be blocked and shall not be operated with excessive deadbands. To provide an equitable and coordinated system response to generation-load imbalances, governor droop shall be set at 5%. (g) A generating unit providing contingency reserve as an ancillary service shall be synchronized with the grid at the start of every trading interval to be able to automatically respond to any sudden loss or significant reduction in generating capacity. (h) In case the system frequency momentarily rises to 62.4 Hz or falls to 57.6 Hz, all generating units shall remain in synchronism with the grid for at least five (5) seconds to allow the System Operator to undertake measures to correct the situation. | Propose to revise as: “(a) The grid frequency shall be controlled by the timely use of frequency regulating reserve during normal conditions, and timely use of contingency reserve, dispatchable reserve and demand control such as automatic load dropping (ALD) and/or manual load dropping (MLD) during alert or emergency conditions. (b) A generating unit providing regulating and/or contingency reserves may be operated either in an automatic frequency-sensitive mode (also known as free governor mode) with as primary response or in an automatic generation control (AGC) mode withas secondary response. xxx (f) Governors shall not be blocked and shall not be operated with excessive deadbands. To provide an equitable and coordinated system response to generation-load imbalances, governor speed-droop shall be set at 5% or better. (g)xxx (h)xxx” | For consistency with PGC2016 GO 6.2.3.5. PR, SR and TR were changed to CR, RR and DR, respectively, in view of the reserve categories used in DC2021-03-0009. For clarity. For consistency with PGC GCR 4.4.2.4.4. |  |  |  |  |
| System Reserve Requirements | 5.8 | (a) Sufficient system reserves shall be available at all times to maintain acceptable system frequency, necessary to cope with any load variations and errors in load forecasting and to replace generating capacity lost due to forced outages of generation and transmission equipment. Adequate frequency regulating reserve and contingency reserve shall be available to stabilize the system and facilitate the restoration to the normal state following a multiple outage contingency. (b) The operating margin of the grid is sufficient if the available generating capacity in excess of the sum of the system demand plus losses is greater than the capacity of the highest synchronized generating unit within a specific period of time to cover loss of a generating unit or the power import from a single circuit interconnection whichever is higher. (c) The required system reserves for regulating and contingency shall be in accordance with the latest ERC approved ancillary service procurement plan. | Propose to revise as follows: “(a) Sufficient system reserves shall be available at all times to maintain acceptable system frequency, necessary to cope with any load variations and errors in load forecasting and to replace generating capacity lost due to forced outages of generation and transmission equipment. Adequate frequency regulating reserve, and contingency reserve, and dispatchable reserve shall be available to stabilize the system and facilitate the restoration to the normal state following a multiple outage contingency. (b) The operating margin of the grid is sufficient if the available generating capacity in excess of the sum of the system demand plus losses is greater than the capacity of the highest synchronized generating unit within a specific period of time to cover loss of a generating unit or the power import from a single circuit interconnection whichever is higher. (c) The required system reserves for regulating, and contingency and dispatchable reserve shall be in accordance with the latest ERC approved ancillary service procurement plan.” | For inclusion of DR, and consistency with the reserve categories used in DC2021-03-0009. |  |  |  |  |
| Demand Control | 5.9 | (a) If demand control due to generation deficiency needs to be implemented, the System Operator shall issue a red alert warning by 1600H, a day ahead. The red alert warning shall specify the amount, the period during which the demand reduction will be required and the reason of the generation deficiency. (b) The System Operator shall issue demand control imminent warning when a demand reduction is expected within the next thirty (30) minutes. The demand control imminent warning shall be effective for one (1) hour and shall be automatically cancelled if it is not re-issued by the System Operator. (c) During demand control, the implementation of real time dispatch shall cease and the System Operator, in coordination with the Market Operator, shall declare market intervention. (d) The user shall provide the System Operator with the amount of demand reduction actually achieved after the implementation of demand control. (e) The user shall abide by the instruction of the System Operator with regard to the restoration of demand. The restoration of demand shall be achieved as soon as possible and the process of restoration shall begin within two (2) minutes after the instruction is given by the System Operator. (f) The demand control shall include the following: (i) Automatic load dropping; (ii) Manual load dropping; (iii) Demand reduction on instruction by the System Operator; and (iv) Voluntary demand management. | Propose to revise as follows: “(a) If demand control due to generation deficiency needs to be implemented, the System Operator shall issue a red alert warning by 1600H, a day ahead. The red alert warning shall specify the amount, the period during which the demand reduction will be required and the reason of the generation deficiency. (b) The System Operator shall issue demand control imminent warning when a demand reduction is expected within the next thirty (30) minutes. The demand control imminent warning shall be effective for one (1) hour and shall be automatically cancelled if it is not re-issued by the System Operator. (c) During demand control, the implementation of real time dispatch shall cease and the System Operator, in coordination with the Market Operator, shall declare market intervention. (d) The user shall provide the System Operator with the amount of demand reduction actually achieved after the implementation of demand control. (e) In the event of a protracted shortage in generation and when a reduction in demand is envisioned by the System Operator to be prolonged, the System Operator shall notify the user of the expected duration. (f) The user shall abide by the instruction of the System Operator with regard to the restoration of demand. The restoration of demand shall be achieved as soon as possible and the process of restoration shall begin within two (2) minutes after the instruction is given by the System Operator. (fg) Demand Control shall be implemented to reduce the Demand of the Grid when: (i) The System Operator has issued a Red Alert notice due to generation deficiency or when a Multiple Outage Contingency resulted in islanding operation; (ii) The System Operator has issued Demand Control Imminent Warning Notice due to generation deficiency; or (iii) There is an Imminent Overloading of a line or Equipment following the loss of a line, equipment or generating plant that poses threat to system Security. (h) The demand control shall include the following: (i) Automatic load dropping; (ii) Manual load dropping; (iii) Demand reduction on instruction by the System Operator; and (iv) Voluntary demand management.” | For consistency with PGC2016 GO 6.6.8 For consistency with PGC2016 GO 6.6.8.4 For consistency with PGC2016, GO 6.6.8.6 Re-numbered due to addition of items (e) and (g). |  |  |  |  |
| Automatic Load Dropping (ALD) and Manual Load Dropping (MLD) | 5.10 | (a) Adequate load shedding facilities initiated automatically by frequency conditions outside the normal operating frequency excursion band shall be available and in service to restore the frequency to normal following the loss of one (1) or more generating units or other significant contingency events. A load shedding program shall be implemented to drop the necessary amount of load to arrest frequency decay, minimize loss of load, and permit timely system restoration. (b) The level of demand required for ALD shall be established by the System Operator in order to limit the consequences of a major loss of generation in the grid. Appropriate technical studies shall be conducted by the system Operator to justify the targets and/or to refine them as necessary. (c) Loads that are subject to ALD shall be split into rotating discrete MW blocks. The number of blocks and the under frequency setting for each block shall be specified by the System Operator. (d) If an ALD has taken place, the affected users shall not reconnect their feeders without clearance from the System Operator. The System Operator shall issue the instructions to reconnect once the frequency of the grid has recovered. (e) To ensure that a subsequent fall in frequency will be contained by the operation of ALD, additional manual load dropping (MLD) shall be implemented so that the loads that were dropped by ALD can be reconnected. (f) MLD shall be conducted by distributors, as directed by the System Operator, in response to an overall shortage of energy at a node or in a region specified in the network market model, or other network conditions as determined by the System Operator in accordance with the procedures established under the Grid Code and Distribution Code. (g) To prepare for a generation deficiency situation, a priority scheme for MLD based on equitable load allocation shall be established by distributors in consultation with the System Operator. (h) Immediately following the issuance by the System Operator of an instruction to implement MLD, distributors shall make arrangement that will enable it to disconnect its scheduled Customers. (i) MLD may also be initiated by the System Operator in response to any other circumstances which it reasonably considers necessitate such action under the Grid Code or Distribution Code or any other applicable regulatory instrument. (j) Customers affected by the MLD shall not be reconnected by distributors until instructed by the System Operator to do so. | Proposed to revise as follows: “(a) Automatic Load Dropping (i) The System Operator shall establish the level of Demand required for Under-Frequency Load Shedding (UFLS) and Under-Voltage Load Shedding (UVLS) in order to limit the consequences of significant incidents or a major loss of generation in the grid. The System Operator shall conduct the appropriate technical studies to justify the targets and/or to refine them as necessary. (ii) A UFLS program shall be planned and implemented in coordination with other UFLS programs, if any, within the Grid and, where appropriate, with neighboring grids. The UFLS program shall be coordinated with generation control and protection systems, Under-voltage and other load shedding programs, Load restoration programs, and transmission protection and control systems. (iii) The user shall prepare its UFLS program in consultation with the System Operator. The user demand that is subject to UFLS shall be split into rotating discrete MW blocks. The System Operator shall specify the number of blocks and the under frequency setting for each block. (iv) If the User does not implement a UFLS program, the Transmission Network Provider shall install the Under-Frequency Relay at the main feeder and the System Operator shall drop the total user demand as a single block, if the need arises. (v) To ensure that a subsequent fall in frequency will be contained by the operation of UFLS, additional Manual Load Dropping shall be implemented so that the loads that were dropped by UFLS can be reconnected. (vi) If a UFLS has taken place, the affected Users shall not reconnect their feeders without clearance from the System Operator. The System Operator shall issue the instruction to reconnect, once the frequency of the grid has recovered. Subject to available generation, the first circuit to trip shall be the first to be energized. (vii) The user shall notify the System Operator of the actual demand that was disconnected by UFLS, or the demand that was restored in the case of reconnection, within five (5) minutes of the load dropping or reconnection. (viii) A UVLS programs shall be planned and implemented in coordination with other UVLS programs in the grid and, where appropriate, with neighboring grids. (ix) All UVLS programs shall be coordinated with generation control and protection systems, UFLS programs, load restoration programs and transmission protection and control programs. (x) The user shall notify the System Operator of the actual demand that was disconnected by UVLS, or the demand that was restored in the case of reconnection, within five (5) minutes of the load dropping or reconnection. (b) Manual Load Dropping (i) The user shall make arrangement that will enable it to disconnect its customer immediately following the issuance by the System Operator of an instruction to implement MLD. (ii) Distribution Utilities shall, in consultation with the System Operator, establish a priority scheme for MLD based on equitable Load allocation. (iii) If the System Operator has determined that the MLD carried out by the user is not sufficient to contain the decline in grid frequency, the System Operator may disconnect the total demand of the user in an effort to preserve the integrity of the grid. (iv) If a user disconnected its customers upon the instruction of the System Operator, the user shall not reconnect the affected customers until instructed by the System Operator to do so. (a) Adequate load shedding facilities initiated automatically by frequency conditions outside the normal operating frequency excursion band shall be available and in service to restore the frequency to normal following the loss of one (1) or more generating units or other significant contingency events. A load shedding program shall be implemented to drop the necessary amount of load to arrest frequency decay, minimize loss of load, and permit timely system restoration. (b) The level of demand required for ALD shall be established by the System Operator in order to limit the consequences of a major loss of generation in the grid. Appropriate technical studies shall be conducted by the system Operator to justify the targets and/or to refine them as necessary. (c) Loads that are subject to ALD shall be split into rotating discrete MW blocks. The number of blocks and the under frequency setting for each block shall be specified by the System Operator. (d) If an ALD has taken place, the affected users shall not reconnect their feeders without clearance from the System Operator. The System Operator shall issue the instructions to reconnect once the frequency of the grid has recovered. (e) To ensure that a subsequent fall in frequency will be contained by the operation of ALD, additional manual load dropping (MLD) shall be implemented so that the loads that were dropped by ALD can be reconnected. (f) MLD shall be conducted by distributors, as directed by the System Operator, in response to an overall shortage of energy at a node or in a region specified in the network market model, or other network conditions as determined by the System Operator in accordance with the procedures established under the Grid Code and Distribution Code. (g) To prepare for a generation deficiency situation, a priority scheme for MLD based on equitable load allocation shall be established by distributors in consultation with the System Operator. (h) Immediately following the issuance by the System Operator of an instruction to implement MLD, distributors shall make arrangement that will enable it to disconnect its scheduled Customers. (i) MLD may also be initiated by the System Operator in response to any other circumstances which it reasonably considers necessitate such action under the Grid Code or Distribution Code or any other applicable regulatory instrument. (j) Customers affected by the MLD shall not be reconnected by distributors until instructed by the System Operator to do so.” | For consistency with PGC2016 GO 6.6.9 (Automatic Load Dropping) and GO 6.6.10 (Manual Load Dropping) |  |  |  |  |
| System Restoration | 5.11 | (a) A coordinated system restoration plan shall be established, reviewed, updated if necessary, and simulated to verify comprehensiveness and feasibility. (b) Following a significant incident that makes it impossible to avoid island grid operation, the grid shall separate into several self-sufficient island grids, which shall be resynchronized to restore the grid to the normal state. (c) If a part of the grid is not connected to the rest of the grid, but there is no blackout in that part of the grid, the resynchronization of that part to the grid shall be undertaken by the System Operator. (d) Sufficient black start and fast start capacity shall be available at strategic locations to facilitate the restoration of the grid to the normal state following a total system blackout. At least two (2) black start plants shall be available at each power restoration highway or sub-grid. Each black start generating unit shall be tested to verify that it can be started and operated without being connected to the system. (e) Emergency drills shall be conducted at least once a year to familiarize all personnel responsible for emergency and grid restoration activities with the emergency and restoration procedures. The drills shall simulate realistic emergency situations. A drill evaluation shall be performed and deficiencies in procedures and responses shall be identified and corrected. | Propose to revise as follows: “(a) A coordinated system restoration plan shall be established, reviewed, updated if necessary, and simulated to verify comprehensiveness and feasibility. (b) Following a significant incident that makes it impossible to avoid islanding grid operation, the grid System Operator shall separate the Grid into several self-sufficient islands grids, which shall be resynchronized to restore the grid to the normal state. (c) If a part of the grid is not connected to the rest of the grid, but there is no blackout in that part of the grid, the System Operator shall undertake the resynchronization of that part to the grid shall be undertaken by the System Operator. (d) Adequate Contingency Reserve and Regulating Reserves shall be available to stabilize the power system and facilitate the restoration to the normal state following a Multiple Outage Contingency. (de) Sufficient black start and fast start capacity shall be available at strategic locations to facilitate the restoration of the grid to the normal state following a total system blackout. At least two (2) black start plants shall be available at each power restoration highway or sub-grid. Each black start generating unit shall be tested to verify that it can be started and operated without being connected to the system. (f) The System Operator shall issue instructions for the generating plants with Black Start Capability to initiate the Start-Up. The generation company providing Black Start shall then inform the System Operator that its generating plants are dispatchable within 30 minutes for the restoration of the Grid. (g) The overall strategy in the restoration of the Grid after a Total System Blackout shall, in general, include the following: (i) Overlapping phases of Blackout restoration of islands; (ii) Step-by-step integration of the Islands into larger subsystems; and (iii) Eventual restoration of the Grid. (h) The System Operator shall inform the Users of the Grid, after completing the Black Start procedure and the restoration of the Grid, that the Blackout no longer exists and that the Grid is back to the Normal State. (ei) Emergency drills shall be conducted at least once a year to familiarize all personnel responsible for emergency and grid restoration activities with the emergency and restoration procedures. The drills shall simulate realistic emergency situations. A drill evaluation shall be performed and deficiencies in procedures and responses shall be identified and corrected. | For consistency with PGC2016 GO 6.2.3.8 For clarity and consistency with PGC GO 6.8.4.2 For consistency with PGC2016 GO 6.2.3.7 and DC2021-03-009. Re-numbering For consistency with PGC2016 GO 6.8.3.2 For consistency with PGC2016 GO 6.8.3.4 For consistency with PGC2016 GO 6.8.3.6 Re-numbering |  |  |  |  |
| Grid Protection Requirements | 5.12 | (a) Grid protection shall be designed, coordinated, tested and maintained to achieve the desired level of speed, sensitivity, and selectivity in fault clearing and to minimize the impact of faults on the grid. | Propose to revise as: “(a) Grid protection shall be designed, wired, set and coordinated such that operation will not occure for external faults or non-fault conditions, tested and maintained to achieve the desired level of speed, sensitivity, and selectivity in fault clearing and to minimize the impact of faults on the grid.” | For consistency with PGC2016 GPR 7.2.3 |  |  |  |  |
|  |  | (b) The grid shall have adequate and coordinated primary (Main 1 and Main 2) and local and remote backup protection at all times to limit the magnitude of grid disturbances when a fault or equipment failure occurs. Preferably, the Main 1 and Main 2 protection should be of different types (e.g. distance relay for Main 1 and current differential relay for Main 2) and use different teleprotection media (e.g. power line carrier or optical fiber for Main 1 and microwave for Main 2). | Propose to revise as: “(b) The grid shall have adequate and coordinated primary (Main 1 and Main 2) and local and remote backup protection at all times to limit the magnitude of grid disturbances when a fault or equipment failure occurs. Preferably, the Main 1 and Main 2 protection should be of different types (e.g. distance relay for Main 1 and current differential relay for Main 2) and use different teleprotection media (e.g. power line carrier or optical fiber for Main 1 and microwave for Main 2). Redundant protection systems shall be installed in identified critical transmission lines. The two main line protection systems must preferably utilize different schemes and communication media.” | For clarity and consistency with PGC2016 GPR 7.2.4 |  |  |  |  |
|  |  | (d) Circuit breaker fail protection shall be designed to initiate the tripping of all the necessary electrically adjacent circuit breakers and to interrupt the fault current within the next fifty (50) milliseconds, in the event that the primary protection system fails to interrupt the fault current within the prescribed fault clearance time. | Propose to revise as: “(d) Circuit breaker failure protection system shall be designed to initiate the tripping of all the necessary electrically adjacent circuit breakers and to interrupt the fault current within the next fifty (50) milliseconds, in the event that after the primary protection system fails to interrupt clear the fault current within the prescribed fault clearance time.” | For consistency with PGC2016 GPR 7.3.3.2.1. |  |  |  |  |
|  |  | (i) Following a credible N-1 contingency where the Rules for a minimum grid performance are compromised, a temporary security measure such as the system integrity protection scheme (SIPS) shall be employed to avoid subsistence and spreading of the disturbance. The temporary employment of SIPS shall be coordinated with the concerned users and shall only be applied specific to parts of the system determined to be exposed to a high degree of likelihood for a secondary contingency (N-1-1) or a subsequent multiple contingency (N-x) such that the risk of cascaded blackout is avoided. Information on all available SIPS shall be provided to the Grid Management Committee and at the same time, it shall be coordinated with the concerned users. | Propose to revise as: “(i) Following a credible N-1 contingency where the Rules for a minimum grid performance are compromised, a temporary security measure such as the system integrity protection scheme (SIPS) shall be employed to avoid subsistence and spreading of the disturbance. The temporary employment of SIPS shall be coordinated with the concerned users and shall only be applied specific to parts of the system determined to be exposed to a high degree of likelihood for a secondary contingency (N-1-1) or a subsequent multiple contingency (N-x) such that the risk of cascaded blackout is avoided. Information on all available SIPS shall be provided to the Grid Management Committee and at the same time, it shall be coordinated with the concerned users SIPS shall be installed to preserve the integrity of the Grid or strategic portions thereof lacking Single Outage Contingency (N-1) security, determined to be exposed to a high degree of probability of a secondary Contingency (N-1-1), and subsequent Multiple Outage Contingency (N-k) during abnormal system conditions such as instability, thermal overloading, and voltage collapse. The prescribed action automatically performed by the schemes to protect system integrity may require the opening of one or more lines, tripping of generators, intentional shedding of Loads, or other mitigation measures that will alleviate the problem. The application of SIPS shall be coordinated with the concerned Users of the Grid and shall only be specific to parts of the system determined to be exposed to a high degree of likelihood for a secondary Contingency (N-1-1) or a subsequent multiple Contingency (N-k) such that the risk of cascaded blackout is avoided.” | For consistency with PGC2016 GPR 7.7.1 and GPR 7.7.5. |  |  |  |  |
| Telecommunications Requirements | 5.13 | Xxx (c) Separate telecommunication channels shall be provided for SCADA, automatic generation control (AGC), protective relaying, special protection systems, voice and data where appropriate. xxx | Propose to revise as: “(c) Separate telecommunication channels shall be provided for SCADA, automatic generation control (AGC), protective relaying, special protection systems, voice and data where appropriate.” | AGC doesn’t require a separate telecom channel to operate. It sends AGC setpoint commands to the generating units and receives feedback signals using the SCADA channel or DAC network. |  |  |  |  |
| Responsibilties | Section 6 | The System Operator shall: (a) Make the necessary manual interventions upon existence of an imminent threat in system security or a credible N-1 contingency to restore back, without delay, the grid operating condition to normal state; |  |  |  |  |  |  |
|  |  | (b) Initiate, upon the existence of a credible N-1 contingency, any or a combination of manual corrective interventions as follows: (i) Switch off, or re-route, energy delivery from a Generation Company; (ii) Call equipment into service; (iii) Take transmission line or equipment out of service; (iv) Commence operation of generating units or maintain, increase or reduce active or reactive power output of the same; (v) Increase, reduce output of generating units or shut down or otherwise vary operation of the same; and shed or restore load; | Propose to revise as: “(b) In case a credible N-1 Contingency occurs in the system and where no temporary System Integrity Protection Scheme (SIPS) are employed to avoid spreading of the disturbance, iInitiate, upon the existence of a credible N-1 contingency, any or a combination of manual corrective interventions as follows below, following a credible N-k Contingency in anticipation of a probable secondary outage, in order to stabilize the system: (i) Generating Unit re-Dispatching Switch off, or re-route, energy delivery from a Generation Company; (ii) Usage of Voltage and/or power flow control on regulation Transformers Call equipment into service; (iii) Network re-configuration Take transmission line or equipment out of service; (iv) Manual Load Dropping (MLD) Commence operation of generating units or maintain, increase or reduce active or reactive power output of the same; or (v) Generating Unit Tripping Increase, reduce output of generating units or shut down or otherwise vary operation of the same; and shed or restore load” | For consistency with PGC2016 GO 6.2.3.3 |  |  |  |  |
|  |  | (d) Constrain-on / constrain-off or make use of MRUs whenever all available ancillary reserves are depleted or exhausted; | Propose to revise as: “(d) Constrain-on / constrain-off generators using the WESM Merit Order Table (WMOT) or make use of MRUs re-dispatched out-of-merit whenever all available ancillary reserves are depleted or exhausted;” | To clarify the use of WMOT for constrain-on/ constrain-off (based on Dispatch Protocol Issue 16.0 Section 10.6.1) while MRUs are dispatched out-of-merit (based on Dispatch Protocol Issue 16.0 Section 11.6.5) |  |  |  |  |
|  |  | (f) Propose a uniform required deadband applicable to all generators; and | Propose to revise as: “Propose a uniform required deadband applicable to all generatingors units providing Contingency Reserve as an Ancillary Service; and” | For consistency with PGC 2016 GCR 4.4.2.4.2 and DC2021-03-009. |  |  |  |  |
|  |  | (g) Issue necessary alert notices upon existence of qualifying threat. | Propose to revise as: “(g) Issue necessary alert notices upon existence of qualifying threat; and” | For clarity |  |  |  |  |
|  |  | NEW | Propose to add: “(I) Maintain the Frequency Response Obligation (FRO) as indicated in the Philippine Grid Code, intended to be the minimum frequency response for preserving the reliability of the Grid.” | For consistency with PGC 2016, GO 6.6.3 |  |  |  |  |

- WESM Rules

| Title | Clause | Provision | Proposed Amendment | Rationale | Comment | Proposed Wording based on Comments | Proponent’s Response | RCC Agreement |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Glosssary | Chapter 11 | AGC. Automatic Generation Control | Propose to revise as follows: “AGC.Automatic Generation Control (AGC). It is an equipment that automatically adjusts the generation to maintain its generation dispatch, interchange schedule plus its share of frequency regulation. AGC is a combination of secondary control for a control area /control block and real-time operation of the generation dispatch function (based on generation scheduling). Secondary control is operated by the System Operator while generation scheduling is operated by the respective generation companies.” | For consistency with the definition in the PGC 2016 Edition. |  |  |  |  |
|  |  | Dispatchable Reserve. Generating capacity that is not scheduled for regular energy supply, regulating reserve, contingency reserve, or interruptible loads not scheduled for contingency reserve, and that are readily available for dispatch in order to replenish the contingency reserve service whenever a generating unit trips or a loss of a single transmission interconnection occurs. | Propose to revise as: “Dispatchable Reserve. Generating capacity that is not scheduled for regular energy supply, regulating reserve, contingency reserve, or interruptible loads not scheduled for contingency reserve, and that are readily available for dispatch in order to replenish the contingency reserve service whenever a generating unit trips or a loss of a single transmission interconnection occurs.” | For consistency with the definition of Dispatchable Reserve in DC2021-03-0009. |  |  |  |  |
|  |  | Normal State. The grid operating condition when: (a) The operating margin is sufficient; (b) System frequency is within the limits as set in the Grid Code; (c) Voltages at all connection points are within the limits of 0.95 and 1.05 of the nominal value; (d) The loading levels of all transmission lines and transformers are below the limit as set in the Grid Code; (e) The grid configuration is such that any potential fault current can be interrupted and the faulted equipment can be isolated from the grid; (f) The static and dynamic stability of the power system is maintained; and (g) The Single Outage Contingency (N-1) Criterion is met.” | Propose to revise as: “Normal State. The grid operating condition when the power system frequency, voltage, and transmission line and equipment loading are within their normal operating limits, the Operating Margin is sufficient, and the grid configuration is such that any fault current can be interrupted and the faulted equipment isolated from the Grid. (a) The operating margin is sufficient; (b) System frequency is within the limits as set in the Grid Code; (c) Voltages at all connection points are within the limits of 0.95 and 1.05 of the nominal value; (d) The loading levels of all transmission lines and transformers are below the limit as set in the Grid Code; (e) The grid configuration is such that any potential fault current can be interrupted and the faulted equipment can be isolated from the grid; (f) The static and dynamic stability of the power system is maintained; and (g) The Single Outage Contingency (N-1) Criterion is met” | For consistency with the definition of normal state in PGC 2016. |  |  |  |  |
|  |  | Reliability. The probability of a system, device, plant or equipment performing its function adequately for the period of time intended, under the operating conditions encountered. | Propose to revise as: “Reliability. The performance of the elements of the bulk electric system that results in electricity being delivered to customers within accepted standards and in the amount desired. Reliability may be measured by the frequency, duration, and magnitude of adverse effects on the electric supply. The probability of a system, device, plant or equipment performing its function adequately for the period of time intended, under the operating conditions encountered.” | For consistency with the definition of Reliability in PGC 2016. |  |  |  |  |

- WESM Manual on Dispatch Protocol Issue 16.0

| Title | Clause | Provision | Proposed Amendment | Rationale | Comment | Proposed Wording based on Comments | Proponent’s Response | RCC Agreement |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Definitions, References and Interpretation | Section 2 | Automatic Generation Control (AGC). The regulation of the power output of generating units within a prescribed area in response to a change in system frequency, tie-line loading, or the relation of these to each other, so as to maintain the system frequency or the established interchange with other areas within the predetermined limits or both. | Propose to revise as follows: “Automatic Generation Control (AGC). It is an equipment that automatically adjusts the generation to maintain its generation dispatch, interchange schedule plus its share of frequency regulation. AGC is a combination of secondary control for a control area /control block and real-time operation of the generation dispatch function (based on generation scheduling). Secondary Control is operated by the System Operator while generation scheduling is operated by the respective Generation Companies. The regulation of the power output of generating units within a prescribed area in response to a change in system frequency, tie-line loading, or the relation of these to each other, so as to maintain the system frequency or the established interchange with other areas within the predetermined limits or both.” | For consistency with the definition in the PGC 2016 Edition. |  |  |  |  |
|  |  | Demand Control. The reduction in demand for the control of frequency when the grid is in an emergency state. This includes automatic load dropping, manual load dropping, demand reduction upon instruction by the System Operator, demand disconnection initiated by users, customer demand management, and voluntary load curtailment. | Propose to revise as: “Demand Control. The reduction in demand for the control of the Frequency when the grid is in an emergency State. This includes automatic load dropping, manual load dropping, demand reduction upon instruction by the System Operator, demand disconnection initiated by users, customer demand management, and voluntary load curtailment. and voluntary demand management. | For consistency with the definition in PGC 2016. |  |  |  |  |
|  |  | NEW | Propose to add: “Islanding Operation. The isolated operation of certain portions of the grid as a result of forced outages or contingency action by the System Operator.” | For reference in the use of “islanding operation” in Table 9 under Section 17.3 and Section 19.1.4 (a). |  |  |  |  |
|  |  | Multiple Outage Contingency. An event caused by the failure of two (2) or more components of the grid including generating units, transmission lines, and transformers. | Propose to revise as follows: Multiple Outage Contingency. An event caused by the failure of two (2) or more components of the grid including generating units, transmission lines, and transformers. | For consistency with the definition in PGC 2016. |  |  |  |  |
|  |  | NEW | Propose to add the following: “Normal State. The grid operating condition when the power system frequency, voltage, and transmission line and equipment loading are within their normal operating limits, the Operating Margin is sufficient, and the grid configuration is such that any fault current can be interrupted and the faulted equipment isolated from the Grid.” | For reference in its use in Sections 7.7.1, 11.5.3, 12.1.3, 12.4.1(c), and Table A of Section 16.13.2. |  |  |  |  |
|  |  | Security. The ability of the electric system to withstand sudden disturbances such as electric short circuits or unanticipated loss of system elements. | Proposed to revise as follows: “Security. The continuous operation of a power system in the normal state, ensuring safe and adequate supply of power to end-users, even when some parts or components of the system are on outageThe ability of the electric system to withstand sudden disturbances such as electric short circuits or unanticipated loss of system elements.” | For consistency with the definition used in PGC 2016 Edition. |  |  |  |  |
|  |  | System Integrity Protection Scheme (SIPS). A protection system that is designed to detect abnormal or predetermined system conditions, and take automatic corrective actions. | Revise as follows: “System Integrity Protection Scheme (SIPS). A protection system that is designed to detect abnormal or predetermined system conditions, and take automatic corrective actions other than and/or in addition to the isolation of faulted components in order to preserve the integrity of the power system or strategic portions thereof.” | For consistency with the definition under the PGC 2016. |  |  |  |  |

Note: Please underline and put in bold letters the proposed changes to the Market Rules or Manual.