[image: image1.jpg]Wholesale Electricity
Spot Market



                      





     
                                                                                   WESM-WM-(Manual)-CN - ______
REQUEST FOR AMENDMENTS OR CHANGES TO THE WESM MANUALS
Proposals made only under this prescribed form shall be accepted and considered as submitted: 
This request for amendments to the WESM Rules can be submitted to:

PEM Board
Attention: PEM Committee Secretariat
Philippine Electricity Market Corporation 

18/F Robinsons Equitable Tower

ADB Avenue, Ortigas Center
Pasig City, 1605 Philippines


Email address: rcc@wesm.ph




Fax Number: (+632) 395-2704
I.  Proponent’s Information
	Name                  
	Jose Mari T. Bigornia

	Designation         
	President and CEO

	Company              
	Independent Electricity Market Operator of the Philippines, Inc.

	Company Address               
	19/F Robinsons Equitable Tower ADB Ave. Ortigas Center


	
	Pasig City


	
	

	Telephone No.                      
	02 318 9376


	Fax. No.
	02 636 0802


	Email Address
	malee.bigornia@iemop.ph


II. WESM Manual Amendments Information
	Title of WESM Manual being commented:

Metering Standards and Procedures Issue 12.0
Nature of Request (please indicate with x)

  FORMCHECKBOX 
 Addition    FORMCHECKBOX 
 Alteration    FORMCHECKBOX 
 Deletion    FORMCHECKBOX 
 Clarification    FORMCHECKBOX 
  Clerical Correction



III. Proposed Amendments
	Title
	Section
	Provision
	Proposed Amendment
	Rationale

	METERING INSTALLATION STANDARDS – METERS – Requirements for Revenue Meters for Embedded Generators Registered as WESM Participants
	2.4.2
	For Embedded Generators registered as WESM Participants, meters installed as the main revenue meter and back-up meter shall adhere to the prevailing requirements of the Philippine Grid Code.
The current specifications are provided as Appendix M of this Manual.
	For Embedded Generators registered as WESM Participants, meters installed as the main revenue meter and back-up meter shall adhere to the prevailing requirements of the Philippine Distribution Grid Code and in 5-minute interval data.
The current specifications are provided as Appendix M of this Manual.
	To incorporate application of PDC standards for embedded generators as provided under Section 5.2.2 of DC2019-02-0003. However, it is proposed that 5-minute interval data be required to match the WESM’s 5-minute dispatch interval since PDC only requires 15-minute interval metering.
Reference to current specifications is proposed to be deleted to remove necessity to revise manual every time the PDC standards are updated.

Note: This proposed amendment was also submitted as a comment on NGCP’s change proposal (ORCP-WM-19-06). 

	METERING INSTALLATION STANDARDS – INSTRUMENT TRANSFORMERS – General Requirements
	2.5.1
	Metering installations shall include instrument transformers.
	Metering installations, if applicable, shall include instrument transformers. 

2.5.1.1 Requirements for Transmission Grid Instrument Transformers

Instrument Transformers used for metering of Transmission Grid Connections shall adhere to the prevailing requirements of the Philippine Grid Code. 
2.5.1.2 Requirements for Embedded Generators Registered as WESM Participants 

Instrument Transformers used for metering of Embedded Generators registered as WESM Participants shall adhere to the prevailing requirements of the Philippine Distribution Code. 
	To incorporate application of PDC standards for embedded generators as provided under Section 5.2.2 of DC2019-02-0003.

Section 7.2.1(b) of the PDC provides that the distribution metering equipment shall include instrument transformers as may be applicable only.

Note: This proposed amendment was also submitted as a comment on NGCP’s change proposal (ORCP-WM-19-06).

	METERING INSTALLATION STANDARDS – COMMUNICATION LINKS FOR THE METER
	2.8
	The communication link to be installed shall be a dedicated line for metering purposes (e.g. PLDT, Bayantel, Digitel lines or GSM Modem) of the MSP.
	The communication link to be installed for metering installations of facilities directly connected to the transmission system shall be a dedicated line for metering purposes (e.g. PLDT, Bayantel, Digitel lines or GSM Modem) of the MSP.
The communication link to be installed for metering installations of facilities directly connected to a distribution system shall comply with the relevant provisions of the Philippine Distribution Code.

	To incorporate application of PDC standards for embedded generators as provided under Section 5.2.2 of DC2019-02-0003.

	METERING INSTALLATION STANDARDS – SECURITY OF METERING INSTALLATIONS AND DATA – General Requirements
	2.9.1
	(inserted)
	General Requirements

Security of metering installations of facilities directly connected to the transmission system shall comply with the requirements of this Section 2.9.

Metering installations of facilities directly connected to a distribution system shall comply with the security requirements of the Philippine Distribution Code.


	To incorporate application of PDC standards for embedded generators as provided under Section 5.2.2 of DC2019-02-0003

	METERING INSTALLATION STANDARDS – SECURITY OF METERING INSTALLATIONS AND DATA
	2.9.1

2.9.1.1

2.9.1.2

2.9.1.3

2.9.1.4

2.9.1.5

2.9.1.6

2.9.1.7

2.9.2

2.9.2.1

2.9.2.2

2.9.2.3

2.9.2.4

2.9.2.5


	2.9.1 XXX

2.9.1.1 XXX

2.9.1.2 XXX

2.9.1.3 XXX

2.9.1.4 XXX

2.9.1.5 XXX

2.9.1.6 XXX

2.9.1.7 XXX

2.9.2 XXX

2.9.2.1 XXX

2.9.2.2 XXX

2.9.2.3 XXX

2.9.2.4 XXX

2.9.2.5 XXX


	2.9.2 XXX

2.9.2.1 XXX

2.9.2.2 XXX

2.9.2.3 XXX

2.9.2.4 XXX

2.9.2.5 XXX

2.9.2.6 XXX

2.9.2.7 XXX

2.9.3 XXX

2.9.3.1 XXX

2.9.3.2 XXX

2.9.3.3 XXX

2.9.3.4 XXX

2.9.3.5 XXX
	Proposed re-numbering with the insertion of new clause 2.9.1

	METERING INSTALLATION STANDARDS – REDUNDANT METERING INSTALLATION
	2.10.4
	(new)
	Facilities directly connected to a distribution system are not required to have redundant metering.
	To incorporate application of PDC standards for embedded generators as provided under Section 5.2.2 of DC2019-02-0003

	SPECIFICATIONS FOR REVENUE METERS FOR EMBEDDED GENERATORS REGISTERED AS WESM PARTICIPANTS
	APPENDIX M
	APPENDIX M

SPECIFICATIONS FOR REVENUE METERS FOR EMBEDDED GENERATORS REGISTERED AS WESM PARTICIPANTS
XXX
	APPENDIX M

SPECIFICATIONS FOR REVENUE METERS FOR EMBEDDED GENERATORS REGISTERED AS WESM PARTICIPANTS

XXX
	Reference to current specifications is proposed to be deleted to remove necessity to revise manual every time the PDC standards are updated.


         Note: For convenience, please underline and put in bold letters the proposed changes to the WESM Manual.
IV. Proposed Scheme to Monitor the Effectiveness of the Proposed Changes to the WESM Manual
	


V.  Referral 

   MAG Date Received:  ________________________    
   Proposed Amendment:          FORMCHECKBOX 
 Urgent          FORMCHECKBOX 
 Minor          FORMCHECKBOX 
 General
A. For Urgent Amendment (For the use of PEMC President only)
	Date Referred to PEMC President
	 FORMCHECKBOX 
 Yes                      FORMCHECKBOX 
 No

	Certifies as urgent
	 FORMCHECKBOX 
 Yes                      FORMCHECKBOX 
 No

	Convene the RCC within 48 hrs.
	

	Remarks:




B. For Minor and General Amendment (For the use of RCC only)
	Date Referred to  RCC:                
	

	Remarks:



	Action taken: 

	Request for comments:
	 FORMCHECKBOX 
  Yes            FORMCHECKBOX 
 No

	
	Request written comments from:
 FORMCHECKBOX 
 DRG           FORMCHECKBOX 
  MSC           FORMCHECKBOX 
  PA           FORMCHECKBOX 
  MO
 FORMCHECKBOX 
 ECO            FORMCHECKBOX 
  RCC           FORMCHECKBOX 
  TC           

 FORMCHECKBOX 
 Other PEM Board Committees  
 FORMCHECKBOX 
  Other Interested Parties 

	For further review of the  Technical Sub-Committee: 
	 FORMCHECKBOX 
 Yes    
Assigned to:
 FORMCHECKBOX 
  SO Sub-Committee
 FORMCHECKBOX 
  MO Sub-Committee

 FORMCHECKBOX 
  Metering Sub-Committee

 FORMCHECKBOX 
  Billing and Settlement Sub-Committee

 FORMCHECKBOX 
  Legal and Regulatory Sub-Committee               

	
	 FORMCHECKBOX 
 No 

	For public consultation: 
	 FORMCHECKBOX 
 Yes             FORMCHECKBOX 
  No  

	RCC Resolution:
	 FORMCHECKBOX 
  Approved         FORMCHECKBOX 
  Disapproved

	RCC Resolution No.:
	

	Date of Resolution:
	

	RCC Meeting No.
	

	Date of endorsement to the PEM Board:
	


PAGE  

